## COWs List
COW ID | Power Source | Shelter Type | Location | Latitude | Longitude | Single Generator Capacity KVA | Single Generator Working-hours Hours | SEC Meter Capacity Amp | Backup Generator Capacity KVA | Backup Generator Working-hours Hours | Rectifier Capacity KW | AC1 Capacity Btu/h | AC1 Age Years | AC2 Capacity Btu/h | AC2 Age Years | Batteries Capacity Ah | Number of Strings Number | Batteries Age Years | Avrage lead-acid Charge Rate c-rate A/Ah | Avrage Lithium disCharge Rate c-rate A/Ah | Telecom Load All KW | Telecom Load inside Shelter KW | Telecom Load All KW | Telecom load heat dissipation KBtu/h | Prime Generator Net Power output KW | Prime SEC Net Power Output KW | Backup Generator Net Power Output KW | Rectifier Net Power Output KW | AC1 Net Cooling Capacity KBtu/h | AC1 Net Power Demand KW | AC2 Net Cooling Capacity KBtu/h | AC2 Net Power Demand KW | Batteries Strings MAX useful capacity Ah | Batteries Strings MAX useful capacity KWh | Batteries Strings MAX useful Time Hours | Batteries Strings Max Charging Current Amp | Batteries Strings Max Charging Power KW | Batteris Strings Min Charing Time Hours | Batteries Strings Max DisCharging Current Amp | Batteries Strings Max DisCharging PowerKW | Batteris Strings Min DisCharing Time Hours | Calculated Discharge Current Amp
CWN105 | SB | Shelter | Arafat | 21.3562 | 39.9848 | 0 | 0 | 100 | 25 | 0 | 18 | 36000 | 0 | 36000 | 0 | 200 | 3 | 0 | 0.5 | 0.8 | 8.4 | 3.6 | 12 | 12283.2 | 0 | 31.28 | 17.4 | 18 | 29880 | 2.5021 | 29880 | 2.5021 | 300 | 15 | 1.25 | 225 | 1.44 | 1.3333 | 60 | 3 | 5 | 240
CWN923 | DG | Shelter | Arafat | 21.3613 | 39.9739 | 35 | 0 | 100 | 35 | 0 | 19.2 | 36000 | 0 | 36000 | 0 | 190 | 5 | 0 | 0.5 | 0.8 | 10.5 | 4.5 | 15 | 15354 | 24.36 | 31.28 | 24.36 | 19.2 | 29880 | 2.5021 | 29880 | 2.5021 | 475 | 23.75 | 1.5833 | 240 | 1.536 | 1.9792 | 95 | 4.75 | 5 | 300
CWN991 | SB | Shelter | Arafat | 21.3722 | 39.9383 | 0 | 0 | 100 | 30 | 0 | 18 | 48000 | 0 | 48000 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 8.4 | 3.6 | 12 | 12283.2 | 0 | 31.28 | 20.88 | 18 | 39840 | 3.3361 | 39840 | 3.3361 | 400 | 20 | 1.6667 | 225 | 1.44 | 1.7778 | 80 | 4 | 5 | 240
CWN076 | SG | Shelter | Arafat | 21.3692 | 39.9771 | 30 | 0 | 0 | 0 | 0 | 15 | 36000 | 0 | 36000 | 0 | 200 | 7 | 0 | 0.5 | 0.8 | 8.4 | 3.6 | 12 | 12283.2 | 20.88 | 0 | 0 | 15 | 29880 | 2.5021 | 29880 | 2.5021 | 700 | 35 | 2.9167 | 187.5 | 1.2 | 3.7333 | 140 | 7 | 5 | 240
CWN108 | SB | Shelter | Arafat | 21.3492 | 39.9837 | 0 | 0 | 100 | 25 | 0 | 18 | 36000 | 0 | 36000 | 0 | 200 | 3 | 0 | 0.5 | 0.8 | 8.4 | 3.6 | 12 | 12283.2 | 0 | 31.28 | 17.4 | 18 | 29880 | 2.5021 | 29880 | 2.5021 | 300 | 15 | 1.25 | 225 | 1.44 | 1.3333 | 60 | 3 | 5 | 240
CWN087 | SB | Shelter | Arafat | 21.3569 | 39.9778 | 0 | 0 | 70 | 35 | 0 | 21 | 36000 | 0 | 36000 | 0 | 190 | 4 | 0 | 0.5 | 0.8 | 8.4 | 3.6 | 12 | 12283.2 | 0 | 21.896 | 24.36 | 21 | 29880 | 2.5021 | 29880 | 2.5021 | 380 | 19 | 1.5833 | 262.5 | 1.68 | 1.4476 | 76 | 3.8 | 5 | 240
CWN075 | SB | Shelter | Arafat | 21.347 | 39.9574 | 0 | 0 | 100 | 35 | 0 | 21.6 | 36000 | 0 | 36000 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 8.4 | 3.6 | 12 | 12283.2 | 0 | 31.28 | 24.36 | 21.6 | 29880 | 2.5021 | 29880 | 2.5021 | 400 | 20 | 1.6667 | 270 | 1.728 | 1.4815 | 80 | 4 | 5 | 240
CWN072 | SB | Shelter | Arafat | 21.342 | 39.976 | 0 | 0 | 100 | 35 | 0 | 16.2 | 36000 | 0 | 36000 | 0 | 295 | 5 | 0 | 0.5 | 0.8 | 8.4 | 3.6 | 12 | 12283.2 | 0 | 31.28 | 24.36 | 16.2 | 29880 | 2.5021 | 29880 | 2.5021 | 737.5 | 36.875 | 3.0729 | 202.5 | 1.296 | 3.642 | 147.5 | 7.375 | 5 | 240
CWN078 | SB | Shelter | Arafat | 21.3405 | 39.9955 | 0 | 0 | 100 | 35 | 0 | 16.2 | 36000 | 0 | 36000 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 8.4 | 3.6 | 12 | 12283.2 | 0 | 31.28 | 24.36 | 16.2 | 29880 | 2.5021 | 29880 | 2.5021 | 400 | 20 | 1.6667 | 202.5 | 1.296 | 1.9753 | 80 | 4 | 5 | 240
CWN084 | SB | Shelter | Arafat | 21.3425 | 39.9622 | 0 | 0 | 100 | 35 | 0 | 21 | 36000 | 0 | 36000 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 10.5 | 4.5 | 15 | 15354 | 0 | 31.28 | 24.36 | 21 | 29880 | 2.5021 | 29880 | 2.5021 | 400 | 20 | 1.3333 | 262.5 | 1.68 | 1.5238 | 80 | 4 | 5 | 300
CWN085 | SB | Shelter | Arafat | 21.3668 | 39.9644 | 0 | 0 | 100 | 35 | 0 | 18 | 36000 | 0 | 36000 | 0 | 190 | 4 | 0 | 0.5 | 0.8 | 8.4 | 3.6 | 12 | 12283.2 | 0 | 31.28 | 24.36 | 18 | 29880 | 2.5021 | 29880 | 2.5021 | 380 | 19 | 1.5833 | 225 | 1.44 | 1.6889 | 76 | 3.8 | 5 | 240
CWN073 | SB | Shelter | Arafat | 21.3738 | 39.9865 | 0 | 0 | 100 | 35 | 0 | 16.2 | 36000 | 0 | 36000 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 11.9 | 5.1 | 17 | 17401.2 | 0 | 31.28 | 24.36 | 16.2 | 29880 | 2.5021 | 29880 | 2.5021 | 400 | 20 | 1.1765 | 202.5 | 1.296 | 1.9753 | 80 | 4 | 5 | 340
CWN093 | SB | Shelter | Arafat | 21.3568 | 39.9353 | 0 | 0 | 200 | 45 | 0 | 15 | 36000 | 0 | 36000 | 0 | 200 | 8 | 0 | 0.5 | 0.8 | 10.5 | 4.5 | 15 | 15354 | 0 | 62.56 | 31.32 | 15 | 29880 | 2.5021 | 29880 | 2.5021 | 800 | 40 | 2.6667 | 187.5 | 1.2 | 4.2667 | 160 | 8 | 5 | 300
CWN083 | SG | Shelter | Arafat | 21.3314 | 39.9655 | 35 | 0 | 0 | 0 | 0 | 18 | 36000 | 0 | 36000 | 0 | 200 | 3 | 0 | 0.5 | 0.8 | 8.4 | 3.6 | 12 | 12283.2 | 24.36 | 0 | 0 | 18 | 29880 | 2.5021 | 29880 | 2.5021 | 300 | 15 | 1.25 | 225 | 1.44 | 1.3333 | 60 | 3 | 5 | 240
CWN102 | SB | Shelter | Arafat | 21.359 | 39.9569 | 0 | 0 | 100 | 45 | 0 | 19.2 | 36000 | 0 | 36000 | 0 | 200 | 8 | 0 | 0.5 | 0.8 | 10.5 | 4.5 | 15 | 15354 | 0 | 31.28 | 31.32 | 19.2 | 29880 | 2.5021 | 29880 | 2.5021 | 800 | 40 | 2.6667 | 240 | 1.536 | 3.3333 | 160 | 8 | 5 | 300
CWN956 | SB | Outdoor | Arafat | 21.3704 | 39.9854 | 0 | 0 | 100 | 25 | 0 | 18 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 17.4 | 18 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1.6667 | 225 | 1.44 | 1.7778 | 80 | 4 | 5 | 240
CWN980 | SB | Outdoor | Arafat | 21.3718 | 39.986 | 0 | 0 | 100 | 25 | 0 | 18 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 17.4 | 18 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1.6667 | 225 | 1.44 | 1.7778 | 80 | 4 | 5 | 240
CWN951 | SB | Outdoor | Arafat | 21.3626 | 39.9691 | 0 | 0 | 100 | 25 | 0 | 15 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 17.4 | 15 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1.6667 | 187.5 | 1.2 | 2.1333 | 80 | 4 | 5 | 240
CWN020 | SB | Outdoor | Arafat | 21.3505 | 39.9681 | 0 | 0 | 100 | 35 | 0 | 24 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 0 | 31.28 | 24.36 | 24 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1.3333 | 300 | 1.92 | 1.3333 | 80 | 4 | 5 | 300
CWN203 | SB | Outdoor | Arafat | 21.3547 | 39.9862 | 0 | 0 | 100 | 35 | 0 | 24 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 24.36 | 24 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1.1765 | 300 | 1.92 | 1.3333 | 80 | 4 | 5 | 340
CWN914 | SB | Outdoor | Arafat | 21.3654 | 39.9717 | 0 | 0 | 100 | 25 | 0 | 15 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 17.4 | 15 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1.6667 | 187.5 | 1.2 | 2.1333 | 80 | 4 | 5 | 240
CWN015 | SB | Outdoor | Arafat | 21.3776 | 39.9868 | 0 | 0 | 100 | 25 | 0 | 18 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 17.4 | 18 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1.6667 | 225 | 1.44 | 1.7778 | 80 | 4 | 5 | 240
CWN212 | SB | Outdoor | Arafat | 21.3661 | 39.9841 | 0 | 0 | 100 | 35 | 0 | 21 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 0 | 31.28 | 24.36 | 21 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1.3333 | 262.5 | 1.68 | 1.5238 | 80 | 4 | 5 | 300
CWN992 | SB | Outdoor | Muzdalifah | 21.3892 | 39.9069 | 0 | 0 | 60 | 25 | 0 | 15 | 10200 | 0 | 0 | 0 | 190 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 18.768 | 17.4 | 15 | 8466 | 0.70893 | 0 | 0 | 380 | 19 | 1.5833 | 187.5 | 1.2 | 2.0267 | 76 | 3.8 | 5 | 240
CWN960 | SB | Outdoor | Arafat | 21.3471 | 39.9926 | 0 | 0 | 100 | 45 | 0 | 21 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 31.32 | 21 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1.6667 | 262.5 | 1.68 | 1.5238 | 80 | 4 | 5 | 240
CWN984 | SB | Outdoor | Arafat | 21.3488 | 39.9957 | 0 | 0 | 100 | 25 | 0 | 18 | 10200 | 0 | 0 | 0 | 190 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 17.4 | 18 | 8466 | 0.70893 | 0 | 0 | 380 | 19 | 1.5833 | 225 | 1.44 | 1.6889 | 76 | 3.8 | 5 | 240
CWN906 | SB | Outdoor | Arafat | 21.3762 | 39.9823 | 0 | 0 | 100 | 30 | 0 | 18 | 10200 | 0 | 0 | 0 | 190 | 4 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 0 | 31.28 | 20.88 | 18 | 8466 | 0.70893 | 0 | 0 | 380 | 19 | 1.2667 | 225 | 1.44 | 1.6889 | 76 | 3.8 | 5 | 300
CWN214 | SB | Outdoor | Muzdalifah | 21.3919 | 39.9037 | 0 | 0 | 100 | 35 | 0 | 18 | 10200 | 0 | 0 | 0 | 190 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 24.36 | 18 | 8466 | 0.70893 | 0 | 0 | 380 | 19 | 1.1176 | 225 | 1.44 | 1.6889 | 76 | 3.8 | 5 | 340
CWN903 | SB | Outdoor | Arafat | 21.3599 | 39.948 | 0 | 0 | 100 | 45 | 0 | 18 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 0 | 31.28 | 31.32 | 18 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1.3333 | 225 | 1.44 | 1.7778 | 80 | 4 | 5 | 300
CWN036 | SB | Shelter | Arafat | 21.3799 | 39.9441 | 0 | 0 | 100 | 45 | 0 | 16 | 48000 | 0 | 48000 | 0 | 190 | 5 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 0 | 31.28 | 31.32 | 16 | 39840 | 3.3361 | 39840 | 3.3361 | 475 | 23.75 | 1.5833 | 200 | 1.28 | 2.375 | 95 | 4.75 | 5 | 300
CWN050 | SG | Shelter | Arafat | 21.3854 | 40.0052 | 35 | 0 | 0 | 0 | 0 | 19.2 | 48000 | 0 | 48000 | 0 | 200 | 2 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 24.36 | 0 | 0 | 19.2 | 39840 | 3.3361 | 39840 | 3.3361 | 200 | 10 | 0.66667 | 240 | 1.536 | 0.83333 | 40 | 2 | 5 | 300
CWN777 | SG | Shelter | Mina | 21.3959 | 39.8997 | 25 | 0 | 0 | 0 | 0 | 16 | 36000 | 0 | 36000 | 0 | 200 | 3 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 17.4 | 0 | 0 | 16 | 29880 | 2.5021 | 29880 | 2.5021 | 300 | 15 | 1.25 | 200 | 1.28 | 1.5 | 60 | 3 | 5 | 240
CWN074 | SB | Shelter | Muzdalifah | 21.3884 | 39.9024 | 0 | 0 | 100 | 35 | 0 | 18.9 | 36000 | 0 | 36000 | 0 | 200 | 2 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 24.36 | 18.9 | 29880 | 2.5021 | 29880 | 2.5021 | 200 | 10 | 0.83333 | 236.25 | 1.512 | 0.84656 | 40 | 2 | 5 | 240
CWN978 | SB | Shelter | Mina | 21.4218 | 39.8919 | 0 | 0 | 100 | 30 | 0 | 18 | 48000 | 0 | 48000 | 0 | 200 | 3 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 20.88 | 18 | 39840 | 3.3361 | 39840 | 3.3361 | 300 | 15 | 1.25 | 225 | 1.44 | 1.3333 | 60 | 3 | 5 | 240
CWN101 | SG | Shelter | Muzdalifah | 21.3884 | 39.9277 | 45 | 0 | 0 | 0 | 0 | 19.2 | 36000 | 0 | 36000 | 0 | 200 | 5 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 31.32 | 0 | 0 | 19.2 | 29880 | 2.5021 | 29880 | 2.5021 | 500 | 25 | 1.4706 | 240 | 1.536 | 2.0833 | 100 | 5 | 5 | 340
CWN068 | SB | Shelter | Muzdalifah | 21.3922 | 39.9124 | 0 | 0 | 100 | 35 | 0 | 24.3 | 36000 | 0 | 36000 | 0 | 200 | 3 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 0 | 31.28 | 24.36 | 24.3 | 29880 | 2.5021 | 29880 | 2.5021 | 300 | 15 | 1 | 303.75 | 1.944 | 0.98765 | 60 | 3 | 5 | 300
CWN089 | SB | Shelter | Muzdalifah | 21.3842 | 39.9108 | 0 | 0 | 100 | 25 | 0 | 15 | 36000 | 0 | 36000 | 0 | 200 | 2 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 17.4 | 15 | 29880 | 2.5021 | 29880 | 2.5021 | 200 | 10 | 0.83333 | 187.5 | 1.2 | 1.0667 | 40 | 2 | 5 | 240
CWN079 | SB | Shelter | Muzdalifah | 21.3615 | 39.9179 | 0 | 0 | 100 | 45 | 0 | 21 | 36000 | 0 | 36000 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 31.32 | 21 | 29880 | 2.5021 | 29880 | 2.5021 | 400 | 20 | 1.1765 | 262.5 | 1.68 | 1.5238 | 80 | 4 | 5 | 340
CWN104 | SB | Shelter | Muzdalifah | 21.3766 | 39.919 | 0 | 0 | 100 | 45 | 0 | 15 | 36000 | 0 | 36000 | 0 | 200 | 3 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 0 | 31.28 | 31.32 | 15 | 29880 | 2.5021 | 29880 | 2.5021 | 300 | 15 | 1 | 187.5 | 1.2 | 1.6 | 60 | 3 | 5 | 300
CWN066 | SB | Shelter | Muzdalifah | 21.3906 | 39.92 | 0 | 0 | 100 | 35 | 0 | 21.6 | 36000 | 0 | 36000 | 0 | 200 | 2 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 24.36 | 21.6 | 29880 | 2.5021 | 29880 | 2.5021 | 200 | 10 | 0.83333 | 270 | 1.728 | 0.74074 | 40 | 2 | 5 | 240
CWN001 | SG | Outdoor | Arafat | 21.3373 | 39.9578 | 30 | 0 | 0 | 0 | 0 | 18 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 20.88 | 0 | 0 | 18 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1.1765 | 225 | 1.44 | 1.7778 | 80 | 4 | 5 | 340
CWN202 | SB | Outdoor | Muzdalifah | 21.397 | 39.9035 | 0 | 0 | 100 | 25 | 0 | 18 | 10200 | 0 | 0 | 0 | 190 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 17.4 | 18 | 8466 | 0.70893 | 0 | 0 | 380 | 19 | 1.5833 | 225 | 1.44 | 1.6889 | 76 | 3.8 | 5 | 240
CWN922 | SB | Outdoor | Muzdalifah | 21.4041 | 39.9161 | 0 | 0 | 100 | 25 | 0 | 15 | 10200 | 0 | 0 | 0 | 190 | 3 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 17.4 | 15 | 8466 | 0.70893 | 0 | 0 | 285 | 14.25 | 1.1875 | 187.5 | 1.2 | 1.52 | 57 | 2.85 | 5 | 240
CWN201 | SB | Outdoor | Mina | 21.4207 | 39.881 | 0 | 0 | 100 | 35 | 0 | 24 | 10200 | 0 | 0 | 0 | 190 | 4 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 0 | 31.28 | 24.36 | 24 | 8466 | 0.70893 | 0 | 0 | 380 | 19 | 1.2667 | 300 | 1.92 | 1.2667 | 76 | 3.8 | 5 | 300
CWN318 | SB | Outdoor | Muzdalifah | 21.3813 | 39.9026 | 0 | 0 | 70 | 35 | 0 | 18 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 21.896 | 24.36 | 18 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1.1765 | 225 | 1.44 | 1.7778 | 80 | 4 | 5 | 340
CWN300 | SB | Outdoor | Muzdalifah | 21.3866 | 39.8971 | 0 | 0 | 100 | 35 | 0 | 21 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 24.36 | 21 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1.1765 | 262.5 | 1.68 | 1.5238 | 80 | 4 | 5 | 340
CWN004 | SB | Outdoor | Muzdalifah | 21.3877 | 39.8962 | 0 | 0 | 100 | 35 | 0 | 24 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 24.36 | 24 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1.1765 | 300 | 1.92 | 1.3333 | 80 | 4 | 5 | 340
CWN998 | SG | Outdoor | Makkah Remote | 21.6472 | 40.3892 | 45 | 0 | 0 | 0 | 0 | 30 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 31.32 | 0 | 0 | 30 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1.1765 | 375 | 2.4 | 1.0667 | 80 | 4 | 5 | 340
CWN967 | SG | Outdoor | Makkah Remote | 21.631 | 40.4272 | 25 | 0 | 0 | 0 | 0 | 33 | 10200 | 0 | 0 | 0 | 100 | 3 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 17.4 | 0 | 0 | 33 | 8466 | 0.70893 | 0 | 0 | 150 | 7.5 | 0.625 | 412.5 | 2.64 | 0.36364 | 30 | 1.5 | 5 | 240
CWN301 | SB | Outdoor | Muzdalifah | 21.3869 | 39.8995 | 0 | 0 | 100 | 35 | 0 | 18 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 0 | 31.28 | 24.36 | 18 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1.3333 | 225 | 1.44 | 1.7778 | 80 | 4 | 5 | 300
CWN008 | SB | Outdoor | Arafat | 21.3514 | 39.9813 | 0 | 0 | 100 | 35 | 0 | 24 | 10200 | 0 | 0 | 0 | 190 | 5 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 24.36 | 24 | 8466 | 0.70893 | 0 | 0 | 475 | 23.75 | 1.3971 | 300 | 1.92 | 1.5833 | 95 | 4.75 | 5 | 340
CWN032 | SB | Outdoor | Muzdalifah | 21.36 | 39.9123 | 0 | 0 | 100 | 45 | 0 | 15 | 10200 | 0 | 0 | 0 | 190 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 31.32 | 15 | 8466 | 0.70893 | 0 | 0 | 380 | 19 | 1.1176 | 187.5 | 1.2 | 2.0267 | 76 | 3.8 | 5 | 340
CWN972 | SB | Outdoor | Muzdalifah | 21.3607 | 39.9162 | 0 | 0 | 100 | 45 | 0 | 18 | 10200 | 0 | 0 | 0 | 190 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 31.32 | 18 | 8466 | 0.70893 | 0 | 0 | 380 | 19 | 1.1176 | 225 | 1.44 | 1.6889 | 76 | 3.8 | 5 | 340
CWN211 | SB | Outdoor | Muzdalifah | 21.3866 | 39.9113 | 0 | 0 | 100 | 35 | 0 | 24 | 10200 | 0 | 0 | 0 | 190 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 24.36 | 24 | 8466 | 0.70893 | 0 | 0 | 380 | 19 | 1.1176 | 300 | 1.92 | 1.2667 | 76 | 3.8 | 5 | 340
CWN953 | SB | Outdoor | Mina | 21.4188 | 39.8927 | 0 | 0 | 100 | 25 | 0 | 18 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 17.4 | 18 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1.6667 | 225 | 1.44 | 1.7778 | 80 | 4 | 5 | 240
CWN959 | SB | Outdoor | Mina | 21.4178 | 39.9104 | 0 | 0 | 100 | 25 | 0 | 18 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 17.4 | 18 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1.6667 | 225 | 1.44 | 1.7778 | 80 | 4 | 5 | 240
CWN976 | SB | Outdoor | Mina | 21.4028 | 39.8975 | 0 | 0 | 100 | 25 | 0 | 18 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 17.4 | 18 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1.6667 | 225 | 1.44 | 1.7778 | 80 | 4 | 5 | 240
CWN994 | SG | Outdoor | Mina | 21.4235 | 39.8953 | 35 | 0 | 0 | 0 | 0 | 15 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 24.36 | 0 | 0 | 15 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1.6667 | 187.5 | 1.2 | 2.1333 | 80 | 4 | 5 | 240
CWN021 | SB | Shelter | Muzdalifah | 21.3934 | 39.9166 | 0 | 0 | 100 | 25 | 0 | 24 | 36000 | 0 | 36000 | 0 | 100 | 3 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 17.4 | 24 | 29880 | 2.5021 | 29880 | 2.5021 | 150 | 7.5 | 0.625 | 300 | 1.92 | 0.5 | 30 | 1.5 | 5 | 240
CWN002 | SG | Shelter | Mina | 21.4204 | 39.8714 | 35 | 0 | 0 | 0 | 0 | 19.2 | 36000 | 0 | 36000 | 0 | 190 | 3 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 24.36 | 0 | 0 | 19.2 | 29880 | 2.5021 | 29880 | 2.5021 | 285 | 14.25 | 0.95 | 240 | 1.536 | 1.1875 | 57 | 2.85 | 5 | 300
CWN961 | SB | Outdoor | Mina | 21.3984 | 39.8973 | 0 | 0 | 100 | 45 | 0 | 18 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 31.32 | 18 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1.1765 | 225 | 1.44 | 1.7778 | 80 | 4 | 5 | 340
CWN997 | SB | Outdoor | Muzdalifah | 21.3831 | 39.9045 | 0 | 0 | 100 | 35 | 0 | 21 | 10200 | 0 | 0 | 0 | 150 | 3 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 24.36 | 21 | 8466 | 0.70893 | 0 | 0 | 225 | 11.25 | 0.66176 | 262.5 | 1.68 | 0.85714 | 45 | 2.25 | 5 | 340
CWN081 | SG | Shelter | Makkah Remote | 20.9935 | 39.5881 | 25 | 0 | 0 | 0 | 0 | 32 | 36000 | 0 | 36000 | 0 | 190 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 17.4 | 0 | 0 | 32 | 29880 | 2.5021 | 29880 | 2.5021 | 380 | 19 | 1.5833 | 400 | 2.56 | 0.95 | 76 | 3.8 | 5 | 240